CITY OF WILBURTON

SPECIAL SCHEDULED MEETING

February 16, 2017

Public Notice posted February 14, 2017, 4:30p.m.

Front Entrance Door, Wilburton City Hall

The Wilburton City Council convened in a SPECIAL Scheduled Meeting held on the 16th day of February, 2017 at 4:30p.m. in the Wilburton City Hall Council chambers; Mayor Stephen Brinlee  presiding.   City Clerk Blankenship was absent; Ms. Chrestman conducted the roll call with members responding:

LITTLEJOHN		PRESENT		MINGS		PRESENT

HAYNES		PRESENT                  	KENDALL	ABSENT

SIMS	              	PRESENT

CITIZEN COMMENTS:     None

- DISCUSS AND TAKE ACTION TO APPROVE OPTION E OR OPTION F FOR INITIAL INTAKE STRUCTURE OF THE FOURCHE MALINE NO. 7M REHABILTATION OF LOYD CHURCH LAKE.

Dale Burke, PE, Infrastructure Solutions Group (ISG), distributed “NRCS Dam Rehabilitation and Intake Structure Report Review Executive Summary”.  He gave a short history stating the dam was built in 1963 using 16 inch reinforced concrete pipe (RC) running through the dam connecting to two 12 inch cast iron pipes, using gravity to feed the raw water to the Water Treatment Plant (WTP). The structure was rehabilitated in 2011 for approximately $95,000. There currently are no pumping costs.

He then presented the 2 alternatives:

Option E:  Floating Intake Structure:  A floating platform with 2 vertical turbine pumps, a level adjustable flexible polyethylene pipe, an 18 inch PVC raw water line and the acquisition of 3-phase power.  This alternative adds pumping costs as all raw water would be pumped to the WTP.  Has an estimated capital cost of $915,600 and an estimated annual operations and maintenance (O&M) cost of $50,903.

Mr. Burke stated he would not recommend a pump on a floating structure as you have to pump 100% of time over dam and to WTP.  Cost to install and operate is prohibitive.

Option F:  Inclined Submersible Pumps:  A pre-fabricated building on the embankment, three 1250 gpm submersible pumps, three 12” polyethylene pipes extending into the lake, and 18 inch raw water line, and acquisition of 3-phase power.  This adds pumping costs as all raw water would have to be pumped to the WTP. Has an estimated capital cost of $1,700,400 and estimated annual O&M cost of $80,343.

Mr. Burke stated it includes building a pit to set in pumps which requires pumping of water 100% of time which will require more excavation on the shore.

Alternative Options:  ISG suggest 2 other options;  1.  Slip-lining the existing 16 inch RC pipe through the dam.  2.  Installing a hybrid siphon/pump floating intake structure.

Mr. Burke stated the Grant Engineers, Guernsey, did not like the slip-lining alternative as it was their opinion it would not work.  He has submitted a letter requesting more technical statistics as to what information led to that conclusion.

Mayor Brinlee stated during the 10 February conference call, NRCS requested an answer.  He explained he did not have the authority to make a decision; it must be presented to the City Council. Grant would fund 70% and City 30% of total costs.

A discussion followed reference current conditions, various options, and several questions concerning costs and possible sources of funding.

MOTION BY HAYNES, SECOND BY LITTLEJOHN TO TABLE ACTION UNTIL A RESPONSE RECEIVED FROM GUERNSEY ENGINEERS PROVIDING MORE TECHNICAL INFORMATION AND DETAIL OF COSTS.

Upon roll call, members present voted as follows:

LITTLEJOHN		Yes		  	MINGS		Yes

HAYNES		Yes			KENDALL	Absent

SIMS			Yes

- ADJOURN:

MOTION BY LITTLEJOHN, SECOND BY HAYNES, TO ADJOURN AT 5:15PM.

Upon roll call, members present voted as follows:

LITTLEJOHN		Yes		  	MINGS		Yes

HAYNES		Yes			KENDALL	Absent

SIMS			Yes

________//ABSENT//____________		             ________________________________

CINDEE BLANKENSHIP, City Clerk	  	STEPHEN BRINLEE, Mayor

___________________________________

ALLEN LITTLEJOHN, Ward 1

___________________________________

TERRY HAYNES, Ward 2

___________________________________

DOUG SIMS, Ward 3

___________________________________

MAE MINGS, Ward 4

_             //ABSENT//__________________

JULIA KENDALL, Ward 5